## Slide 1: Feeder Protection - Pilot Wire & Current Differential
Karl M.H. LAI

## Slide 2: Requirement on Working on Pilot Wire
5.3.12.3
The work or test on pilot cables with risks of triggering the operation of the switching devices shall be carried out by an authorised person who shall receive instructions directly from a control engineer. After the risk has been removed, the work or test on the pilot cable shall be carried out a competent person in accordance with approved procedures.
Add a new rule in CLPP E&M SR
(after Section 5.4.12.2)
1. Risk of Triggering Switching Device by cutting a wrong pilot (Solkor)
2. Risk of Channel Defective Alarm leading to Forced Outage (GRL150)
AP shall make sure the risk of triggering switching device is removed to allow CP with adequate knowledge perform the task
PSOM2201 – Precautions for Working on Transmission and Distribution Pilot Cable or Fibre Optic Cable
Inform all users to divert their channel (protection, intertrip, oil alarm, PSA) before work.
Inform SO before work.
Accept monitoring alarm (MA) before work.
# Require AP to identify the pilot core / cable if there is no clear identification.
TI115 – Avoidance of Danger from Induced Voltage when Working on Cable
Insulated working shall be carried out, as appropriate, with the use of effective combination of any two of the following approved items,
Insulation Mat / Insulation Boot
Insulation Gloves
Insulation Tools
# All tools / equipment must be inspected for any damage and defects before use and any tools / equipment found faulty must be withdrawn from service.

## Slide 3: Pilot Wire Protection in Circuit
Rpp = 490Ω
Rpp
RL
Pilot Loop Resistance = 1000Ω
Ra = 1.9kΩ
Ra = 1.9Ω
Pilot Continuity = 4.8kΩ
Minimum 4 pair cores for 71-72
> 2MΩ at 500V Megger (71 – E, 72 – E, 71 – 72)
R = 8.3Ω/km, C = 60nF/km
Summation CT:
RY : YB : BN = 1: 1: 3
VRE : VYE : VBE = 5: 4: 3
IRE: IYE : IBE = 12: 15: 20
VK > 50 + IF / N (RCT + 2RL)
71
72
R
Y
B
N
Relay Side
T B
PMB
4VYE
5VRE
3VBE
VX

## Slide 4: Pilot Wire Relay (Solkor Vs HOR4)
PILOT WIRE PROTECTION RELAY (HOR4)
6
7
8
9
10
A11
A31
A51
A71
20
17
18
19
T3
T4
RPP
1
2
11
12
13
14
K1
K3
K1
K11
K1
K43
TRIPPING
PILOT WIRE
PW REPEAT
(for alarm & BFP)
INTERTRIPPING (for HSI or Pilot Intertrip Send)
PILOT WIRE PROTECTION RELAY
(SOLKOR RF – VEDETTE CASE)
10
9
8
7
A11
A31
A51
A71
12
T3
T4
RPP
3
4
15
16
1
2
K1
K3
K1
K11
K1
K43
N
N1
TRIPPING
PILOT WIRE
PW REPEAT
(for alarm & BFP)
INTERTRIPPING (for HSI or Pilot Intertrip Send)
RA
5
11

## Slide 5: Pilot Wire Relay (Translay S)
A hybrid relay using hard wire circuit and signal processors.
Component
MBCI : Differential Relay
Phase comparison relay comparing (2IX + IY) and (IX + 2IY)
MRTP: Supervision Relay
Detect pilot open / close condition by DC injection through the pilot loop
MCRI: Overcurrent Relay
“OC start” contact to energize BI at MBCI for differential operation to avoid unstable operation at pilot open condition
MVTW: Destabilizing Relay
Provide a short path to drain out current at To so that no current can be compared, while opening the pilot.
Inject an 80Hz 20mA to remote end for Intertripping.

## Slide 6: Pilot Wire Relay (Translay S)
Phase Comparator based on Coincident Principle
I1
I2
I1 : I2 = RO : (2RPP + RO)
IIN : I1 = (2RO + 2RPP) : RO
I3
IIN
I3 : IIN = (TO I2 – Tr I1) : (2RO + 2RPP)/RO x I1
I1 : restraining (stabilizing) effect to remote end
I2 : operating component
Open Pilot
Effect of Open Pilot
All current goes into operating winding TO.
Short Pilot
Effect of Short Pilot
Increased current at restraining winding Tr.

## Slide 7: Pilot Wire Relay (Translay S)
Equivalent Circuit of Translay S
S1 = IX – 2 IP
Assume RO = RP , then
S1 = IX – 2 (IX / 3 + IY / 3)
Neglecting the multiple factor (x3)
S1 = IX – 2 IY or S1 / IY = IX / IY – 2
S2 = 2/3 IX – 1/3 IY
Similarly, S2 = 2 IX – IY or S2 / IY = IX / IY – 0.5
Stability Zone
Assumption: Tr = 2TO and RO = RP (pilot loop resistance).
The phase comparator has angular limits of ±90o giving a circular characteristics.
For values of 0.5 < IX / IY < 2.0 and phase differences exceeding 90o between S1 and S2, The system is stable.

## Slide 8: Pilot Wire Protection Setting
Type of fault | Operating Current [A] in Secondary |  |  | 
Type of fault | Pilot Normal | Actual Pickup | Pilot Open | Pilot Short
A-E | 0.25 | 0.235 | 0.125 | 1.375
B-E | 0.32 | 0.294 | 0.16 | 1.75
C-E | 0.42 | 0.392 | 0.21 | 2.375
A-B | 1.25 | 1.18 | 0.625 | 7.25
B-C | 1.25 | 1.18 | 0.625 | 7.25
A-C | 0.62 | 0.588 | 0.32 | 3.625
ABC | 0.72 | 0.678 | 0.36 | 4.125
# Through Fault 50x Current Stable
Effect of Load Current
Effect of Pilot Capacitance

## Slide 9: Pilot Wire Protection Condition
Internal Fault:
+
+
External Fault:
+
-
Open Pilot:
+
-
Pilot Low Insulation:
+
-
Open
Shorted
# Normal Load Condition – not operate
# Faulted Condition – may mal-operate
# Relay Mal-operates when IR > Ipickup
# Diode are forward biased at diff. half cycle.

## Slide 10: Pilot Wire Stability Test
A
DC Op Coil Current
AC/ DC Pilot Current
A
A
A
+
+
+
+
+
+
Pilot Normal
Pilot Open
Pilot Crossed
Condition | Op Coil DC Current | Pilot AC Current | Pilot DC Current
Before Test | 5 mA | 4.75 mA | 0.09 mA
Pilot Open | 7.45 mA | 6.81 mA | 0.01 mA
Pilot Crossed | 6.45 mA | 5.29 mA | 2.56 mA
Pilot Normal | 4.85 mA | 4.75 mA | 0.12 mA
Detected by Pilot Continuity Test
Secondary Injection Test Result

## Slide 11: Pilot Wire Protection – Setting Requirement
The following data is required –
Power System Voltage and Frequency
Method of system earthing to determine effective zero sequence charging current during earth faults.
Effective source impedance to calculate maximum internal fault levels and relate these to CT and relay short time rating
Feeder length and impedance to calculate maximum through-fault levels for CT requirement.
In-zone capacitance current to determine minimum allowable fault setting
Load current of feeder to check continuous rating and assess against minimum fault setting for load bias effect.
Minimum fault current for phase and earth-faults to check that they are at least twice the obtained settings.
CT ratio, excitation curve, winding resistance and loop lead burden resistance for CT’s at each end to check CT requirement.
Pilot resistance, pilot capacitance and route length to check against limits and effect upon settings.
Pilot insulation level between cores to check against required value of 500 volts.
Pilot insulation level between cores and earth to check with estimated induced voltage and earth-shift voltage levels.
12. Details of any tapped transformers to check against 20% limit.

## Slide 12: Current Differential Relay
Trip Logic
IL > 400A
Trip
Stay Close if no TR1
Any Trip
Any Trip
Weak Source
Strong Source
DIFF PROT. (0.3A)
&
DIFF PROT. (0.3A)
OC CHECK (1.0A) / EF CHECK (0.3A)
&
BBZ / RMU CC Trip
OC CHECK (0.3A)
&
&
BBZ / RMU CC Trip
OC CHECK (0.3A)
OC CHECK (1.0A) / EF CHECK (0.3A)
OR
OR
DIFF TRIP
PIT TRIP
IR < 400A
Feeder Fault, Diff Trip
Busbar Fault
CC Fault, PIT Trip
IL
IR = 0
Optical Interface MUX-64
Telecom MUX
G.703
G.703
FOC
FOC
Optical Interface MUX-64
Telecom MUX
  Phase-segregated differential protection
  Current setting = DIFI1 = 30% (120A)
  Blocked by Channel Failure & Inrush Current (2nd harmonic)
  Different CT ratios and relay rated currents at 2 ends
  Differential inter-tripping (Transfer trip 1)
  Operating time = 30ms (FO channel)
  Operating time = 40ms (PW channel)
  OC Check for Diff.: OC5 = 100%
  No mal-tripping when CT polarity reversed, CT wiring loosen, or differential protection mal-operates
  CB at weak-infeed end will not trip  Need differential Inter-tripping

## Slide 13: Concepts in Current Differential Relay
Define restraint current and differential current as:
IL
IL
IF
IIN
IO
Case 1: Internal Fault
Case 2: External Fault
IL
IL
IF
IIN
IO
Case 3: External Fault with 1 CT saturated
IL
IL
IF
IIN
IO
IL
IL
IF
IIN
IO
Case 4: Normal Load
IL
IL
IIN
IO

## Slide 14: Concepts in Current Differential Relay
From last page,
ID
IR
IF
External Fault
Internal Fault
IO < 0
CT saturation through fault Locus
External Fault (CT saturate)
Normal Load
Case 1: Increasing Load Current IL
ID
IR
IF
External Fault
Internal Fault
IO < 0
CT saturation through fault Locus
External Fault (CT saturate)
Normal Load
No load (IL = 0)
Case 2: Increasing Fault Current IF
ID
IR
IF
External Fault
Internal Fault
IO < 0
CT saturation through fault Locus
External Fault (CT saturate)
Normal Load
No load (IL = 0)
IF
IL

## Slide 15: Concepts in Current Differential Relay
Case 3: Degree of CT Saturation
ID
IR
IF
External Fault
Internal Fault
IO < 0
CT saturation through fault Locus
External Fault (CT saturate)
Normal Load
No load (IL = 0)
IF
IL
IL , IF
Setting 1: DIFI1
ID
IR
IF
External Fault
Internal Fault
IO < 0, Reverse Current
External Fault (CT saturate)
Normal Load
Restraint
Operate
DIFI1
Note: 3*Charging + Tee-off < DIFI1 < 1/3 Min Fault - cater for CT errors, Tee off and Charging
Setting 2: Slope 1
Note: CT error increases with input current Hence, 1/6 slope 1 setting is provided.  Why 1/6 ?
ID
IR
IF
External Fault
Internal Fault
IO < 0, Reverse Current
External Fault (CT saturate)
Normal Load
Restraint
Operate
DIFI1
Slope 1

## Slide 16: Concepts in Current Differential Relay
ID
IR
IF
External Fault
Internal Fault
IO < 0, Reverse Current
External Fault (CT saturate)
Normal Load
Restraint
Operate
DIFI1
Increasing Load current
Through Fault CT saturation
Observation
Some points are not differentiable. CT saturation in through fault OR Internal fault with increasing load?
Recall internal fault:
Let’s have a setting 2 DIFI2, not trip until overload, and trip at high CT saturation (i.e. nearly no output/ 50% output of ideal).
DIFI2 > IFL (No overload)
2DIFI2 < IF / 2 (CT saturate) (CT output only left 50%)
Hence,
.
Q1: Slope 2 = 1 is a must?
Q2: What is the best separation line for the two sets of dots?
ID
IR
IF
External Fault
Internal Fault
IO < 0, Reverse Current
External Fault (CT saturate)
Normal Load
Restraint
DIFI1
Slope 1
Operate
Slope 2
ID = IR – 2 DIFI2
– 2 DIFI2

## Slide 17: Concepts in Current Differential Relay
ID
IR
IF
External Fault
Internal Fault
IO < 0, Reverse Current
External Fault (CT saturate)
Restraint
Operate
DIFI1
2DIFI2
Tuning DIFI2
Tuning
Summary:
Siemen 7SD610 Line Differential Relay:
Problem: Is ID – IR characteristics unique? What is the benefits with this setting?
Old
New
https://en.ppt-online.org/55658
Setting Consideration –
Minimum Fault Level
Circuit Charging Current
Circuit Length
System Voltage
CT Ratio

## Slide 18: Current Differential - GRL100 Logic
OC Local Guard before sending PIT
Diff Element + OC Guard
Trip upon 1) Diff. + OC Guard 2) PIT Rec. (from remote PIT Send by HZBBZ/CC) 3) CD Rec. (from remote Diff + OC Guard)

## Slide 19: Intertrip in History - Unstabilizing
Distance Protection Acceleration (DPA)
Trip instantaneously with Zone 2 fault
Pilot Opening / Unstabilizing Pilot
Trip instantaneously with open pilot current
RMU CC Operates
Pilot Opening Relay N.C. contact opens
Solkor Open Pilot
Remote S/S trips with open pilot current
CD – Permissive Intertrip
Trip instantaneously with “local” current check

## Slide 20: Direct Transfer Trip (DTT) Vs Permissive Intertrip (PIT)
Provide a +ve by
BBZ Repeat relay
SHE132
MOB132
Tripped by HZBBZ
To avoid the line left energized after HZBBZ, inter-tripping facilities is provided
Any Trip Contact operates with PIT receive as well.
Do we need to have current check before tripping?
No  Direct Transfer Trip (DTT)
Yes  Permissive Intertrip (PIT)